Electron-Ion Collider, Requirements, Specifications, and Interfaces

Interface Control Document: [###]

Detector Infrastructure Systems (6.03.01.09) to IR System Installation and Final Integeration (6.04.04)

Prepared by:

{{Sig_es_:signer1:signature}}	Date: {{Dte_es_:signer1:date}}

Name, Role

Electron-Ion Collider at Institution

Reviewed by:

{{Sig_es_:signer2:signature}}	Date: {{Dte_es_:signer2:date}}

Name, Role

Electron-Ion Collider at Institution

{{Sig_es_:signer3:signature}}	Date: {{Dte_es_:signer3:date}}

Name, Role

Electron-Ion Collider at Institution

{{Sig_es_:signer4:signature}}	Date: {{Dte_es_:signer4:date}}

Name, Role

Electron-Ion Collider at Institution

Approved by:

{{Sig_es_:signer5:signature}}	Date: {{Dte_es_:signer5:date}}

Name, Role

Electron-Ion Collider at Institution

REVISION HISTORY

| Revision # | Effective Date | Additional Reviewers | Summary of Change |
| --- | --- | --- | --- |
| 00 |  |  | Initial release. |

TABLE OF CONTENTS

1.	Purpose and Scope	5

2.	Introduction	5

2.1	Detector Infrastructure Systems	5

2.2	Overview of Interface Relationships	6

2.3	Safety and Environmental Considerations	7

2.4	Design Considerations	7

2.5	Organization	11

3.	Interface summary	11

4.	Detector Infrastructure Systems (DET-INF) to IR System Installation and Final Integeration (IR-SI)	13

5.	Applicable Documents	15

6.	Detailed change Log	15

7.	References	16

LIST OF ACRONYMS

| B0 | B0 is the name of the forward magnet just past the Hadron Endcap |  |
| --- | --- | --- |
| CDR | Conceptual Design Report |  |
| COTS | Commercial Off the Shelf |  |
| DAQ | Data Acquisition |  |
| DET | EIC Detector |  |
| DIRC | Detection of Internally Reflected Cherenkov Light |  |
| dRICH | Dual radiator ring imaging Cherenkov |  |
| DVCS | Deeply Virtual Compton Scattering |  |
| EIC | Electron-Ion Collider |  |
| EMCAL | Electro-magnetic Calorimeter |  |
| ESR | Electron Storage Ring |  |
| FCC | Federal Communications Commission |  |
| FDR | Final Design Review |  |
| GEM | Gas Electron Multiplier |  |
| HCAL | Hadronic Calorimeter |  |
| HSR | Hadron Storage Ring |  |
| HVAC | Heating/Ventilation/Air Conditioning |  |
| IP | Interaction Point |  |
| IR | Interaction Region |  |
| MPGD | Micro Pattern Gaseous Detectors |  |
| NAS | National Academy of Sciences |  |
| NEC | National Electric Code |  |
| NEMA | National Electrical Manufacturers Association |  |
| NFPA | National Fire Protection Association |  |
| NRTL | Nationally Recognized Testing Laboratory |  |
| PID | Particle Identification |  |
| PRR | Production Readiness Review |  |
| PWO | PbWO4 |  |
| RCS | Rapid Cycling Synchrotron |  |
| TBD | To Be Determined |  |
| UL | Underwriter Laboratories |  |
| WBS | Work Break Down Structure |  |

# Interface Control Document:

Detector Infrastructure Systems (6.03.01.09) to IR System Installation and Final Integeration (6.04.04)

# Purpose and Scope

This document records the agreed upon interfaces between the Detector Infrastructure Systems and other sub-systems within the IR System Installation and Final Integeration. These interfaces are based on the system requirements that are necessary to integrate these sub-systems as part of the Electron Ion Collider Project.

# Introduction

These interfaces describe the relationships between the Detector Infrastructure Systems and the IR System Installation and Final Integeration and are divided into two key areas:

Detector Envelope Definition and Control: this includes issues such as physical dimensions of components, interface locations, clearances, keep-out zones, dynamic movements, material deflections, weight distribution, integration, accessibility, and environmental constraints.

Resource Provisioning and Distribution: this includes the provisioning and distribution of resources such as power, cooling, low-conductivity water, cryogens, fluids, gases, etc., as well as the removal of waste energy (heat) and material.

## Detector Infrastructure Systems

Detector infrastructure represents a broad collection of interfaces that tie together all of the subsystems within the detector.  As stated in the introduction, the interfaces within the detector are largely divided into the two categories below.

### Detector Envelope Definition and Control

The subsystem envelopes define the allowable three-dimensional space within which each subsystem must remain throughout all phases of integration, operation, and maintenance. This includes its physical geometry, mounting features, keep-out zones, and any expected motion, growth, or displacement under environmental loads. Together, these controls ensure that all subsystems can be integrated without conflict, maintain required clearances under all operating conditions, and support reliable system-level performance and maintainability.

The envelope controls:

Physical Dimensions and Shape:

Establishes maximum external dimensions and geometric boundaries to ensure all subsystems fit within the allocated volume without interference.

Mounting and Interface Locations:

Specifies the locations and tolerances of mechanical interfaces, fasteners, alignment features, and support structures to ensure compatibility with adjoining subsystems.

Clearances and Keep-Out Zones:

Defines required separation distances from adjacent subsystems, cables, access paths, and structural elements. These zones prevent physical interference during assembly, operation, or service.

Dynamic Movements and Deflections:

Accounts for expected deflections, vibration-induced motion, thermal expansion, and any mechanism actuation, ensuring that no part of the subsystem encroaches beyond the approved boundary.

Mass Properties Placement:

Constrains the placement of high-mass components within the envelope to maintain the system’s mass distribution, center of gravity, and structural loading requirements.

Integration and Accessibility Requirements:

Ensures adequate access for installation, alignment, cabling, inspection, and removal without violating adjacent subsystem envelopes.

Environmental Constraints:

Identifies any volume needed for thermal insulation, shielding, or other environment-driven additions that must be accounted for in the overall system layout.

### Resource Provisioning and Distribution

These interfaces describe how material, energy, and waste are exchanged between the larger, external infrastructure and the detector, and between each of the subsystems within the detector. While the detector envelope identifies the various openings and pathways that will exist, these interfaces describe the physical mechanisms that must be accommodated, what they will carry, and how they will potentially interact or interfere with one another.

        - External Infrastructure

These interfaces include the coordination of incoming cryogenic supply and return connections, low conductivity water services, bulk power to the switchboards, and any other resource that is between the detector and an external system.

Internal Infrastructure

These interfaces describe how energy, material and waste are exchanged between the detector’s subsystems. This includes the internal distribution of power, cooling water, data cabling, fluids, gases, and other materials, as well as the removal of waste heat, fluids, and gases that may accumulate within the detector.

## Overview of Interface Relationships

The following are the sub-systems within the IR System Installation and Final Integeration that have interfaces connected to the Detector Infrastructure Systems.

IR System Installation and Final Integeration (IR-SI): Identify the general types of interface relationships between the ICD reference system and this sub-system.

## Safety and Environmental Considerations

For all materials and components, safety factors will be calculated based on yield strength. As detailed in the infrastructure requirements, parts (excluding bolts) with a safety factor or 3 or greater will generally be accepted without further review, while parts with a safety factor between 1.5 and 3 will require an internal review to determine acceptability.  Any part with a safety factor below 1.5 will be considered unacceptable.

For bolts, a safety factor of 2 or higher may be accepted without further review, while bolts with a safety factor between 1 and 2 must undergo an internal review to determine acceptability. Bolts with a safety factor of 1 or below will be consider unacceptable.

Note, that engineering judgement may be used in unique situations where a needed component goes below the prescribed safety factor.

In all cases, wherever applicable, governing industry standards will guide the design and construction of all infrastructure components. In the absence of a governing standard, the applicable policies of the Department of Energy or Brookhaven National Laboratory will be used.

## Design Considerations

This section contains the current design considerations for the detector infrastructure.

### Detector Envelopes

The following figures illustrate the physical space constraints within the detector.  These diagrams include significantly more detail than is included in the interface definitions and should provide clarity as to how the defined space interfaces were established.

Color Code Legend for Detector Components

Cross-sectional View of Detector Envelopes

End View of Detector Envelopes

Cross-sectional View of Internal Detector Subsystems

## Organization

The interfaces in this document are grouped by sub-system as identified in the sub-system identifier. All interfaces between the Detector Infrastructure Systems and a related sub-system will be included in a single section. Entries within that section will be sorted by the interface identifier or WBS number, as appropriate.

# Interface summary

This tables in this section provide a list of all interfaces that are defined within this document. The interfaces are grouped by sub-system/WBS. Each table has the following fields:

Section: the section number in this document where the interface is addressed.

WBS (1): the WBS number within the ICD reference system, unless the reference system is the owner.

WBS (2): the WBS number for the connected system.

ID: the interface identifier as defined in the Interface Requirement Document (IRD).

Name: the name of the interface as defined in the IRD.

Description: the description of the interface as defined in the IRD.

Owner: identifies the WBS number of the entity that is responsible for ensuring the interface is provided and that it meets validation/verification requirements.

Detector Infrastructure Systems to IR System Installation and Final Integeration

| Section | WBS1 | WBS2 | ID | Name | Description | Owner |
| --- | --- | --- | --- | --- | --- | --- |
| 4 |  | 6.04.04 |  |  | IR System Installation and Final Integeration |  |
| 4.1 | 6.03.01.09 | 6.04.04 | I-DET-INF-INT.011 | Position Constraint | The Low-Q2 detector must be at the same level as the electron beamline. | 6.03.01.09.04 |
| 4.2 | 6.03.01.09 | 6.04.04 | I-DET-INF-INT.041 | Process Cooling | A cooling system will be required to remove heat from the B0-calorimeter and electronics readouts, to maintain an acceptable temperature. A chiller should be installed near the sub-system and a space should be allocated for this chiller. | 6.03.01.09.04 |
| 4.3 | 6.03.01.09 | 6.04.04 | I-DET-INF-INT.115 | LHE Flow (Hall) | A supply and return of liquid helium must be provided to the experimental hall for cooling the solenoid magnet during operation. | 6.03.01.09.04 |
| 4.4 | 6.03.01.09 | 6.04.04 | I-DET-INF-INT.116 | LHE Flow (Assembly Area) | A supply and return of liquid helium must be provided to the assembly hall for cooling the solenoid magnet during maintenance. | 6.03.01.09.04 |
| 4.5 | 6.03.01.09 | 6.04.04 | I-DET-INF-INT.126 | Cryogenic Service Platform (Hall) | A cryogenic service platform must be provided in the experimental hall to support the detector cryogenics interface cryostat that services the interaction region. | 6.03.01.09.04 |
| 4.6 | 6.03.01.09 | 6.04.04 | I-DET-INF-INT.127 | Cryogenic Service Platform (Assembly Area) | A cryogenic service platform must be provided in the assembly hall to support the detector cryogenics interface cryostat that services the maintenance area. | 6.03.01.09.04 |
| 4.7 | 6.03.01.09 | 6.04.04 | I-DET-INF-INT.134 | Hadron Polarimetry Facility | Adequate space must be provided in the interaction region to support the hadron pC-polarimetry components and facility. | 6.03.01.09.04 |

# Detector Infrastructure Systems (DET-INF) to IR System Installation and Final Integeration (IR-SI)

I-DET-INF-INT.011	Position Constraint

System 1:	Low Q2 Detectors (6.03.01.10)

System 2:	IR System Installation and Final Integeration (6.04.04)

Type:	SPACE

Description:	The Low-Q2 detector must be at the same level as the electron beamline.

Provider:	Detector Infrastructure and Utilities Integration (6.03.01.09.04)

Details:	See details in the Detector Infrastructure Interface Control Document.

Requirements:	P-DET-ANC.1

References:

I-DET-INF-INT.041	Process Cooling

System 1:	B-Zero Detectors (6.03.01.10)

System 2:	IR System Installation and Final Integeration (6.04.04)

Type:	SPACE

Description:	A cooling system will be required to remove heat from the B0-calorimeter and electronics readouts, to maintain an acceptable temperature. A chiller should be installed near the sub-system and a space should be allocated for this chiller.

Provider:	Detector Infrastructure and Utilities Integration (6.03.01.09.04)

Details:	See details in the Detector Infrastructure Interface Control Document.

Requirements:	P-DET-ANC.3

References:

I-DET-INF-INT.115	LHE Flow (Hall)

System 1:	Solenoid Magnet (6.03.01.06)

System 2:	IR System Installation and Final Integeration (6.04.04)

Type:	CRYO

Description:	A supply and return of liquid helium must be provided to the experimental hall for cooling the solenoid magnet during operation.

Provider:	Detector Infrastructure and Utilities Integration (6.03.01.09.04)

Details:	See details in the Detector Infrastructure Interface Control Document.

Requirements:	P-DET-MAG-CCR.1, P-DET-MAG-CCR.2, P-DET-MAG-CCR.3, P-DET-MAG-CCR.4, P-DET-INF-CRYO.1, P-DET-INF-CRYO.2, P-DET-INF-CRYO.3, P-DET-INF-CRYO.4

References:

I-DET-INF-INT.116	LHE Flow (Assembly Area)

System 1:	Solenoid Magnet (6.03.01.06)

System 2:	IR System Installation and Final Integeration (6.04.04)

Type:	CRYO

Description:	A supply and return of liquid helium must be provided to the assembly hall for cooling the solenoid magnet during maintenance.

Provider:	Detector Infrastructure and Utilities Integration (6.03.01.09.04)

Details:	See details in the Detector Infrastructure Interface Control Document.

Requirements:	P-DET-MAG-CCR.1, P-DET-MAG-CCR.2, P-DET-MAG-CCR.3, P-DET-MAG-CCR.4, P-DET-INF-CRYO.1, P-DET-INF-CRYO.2, P-DET-INF-CRYO.3, P-DET-INF-CRYO.4

References:

I-DET-INF-INT.126	Cryogenic Service Platform (Hall)

System 1:	Detector Infrastructure and Utilities Integration (6.03.01.09.04)

System 2:	IR System Installation and Final Integeration (6.04.04)

Type:	MECH

Description:	A cryogenic service platform must be provided in the experimental hall to support the detector cryogenics interface cryostat that services the interaction region.

Provider:	Detector Infrastructure and Utilities Integration (6.03.01.09.04)

Details:	See details in the Detector Infrastructure Interface Control Document.

Requirements:	F-DET-INF.3

References:

I-DET-INF-INT.127	Cryogenic Service Platform (Assembly Area)

System 1:	Detector Infrastructure and Utilities Integration (6.03.01.09.04)

System 2:	IR System Installation and Final Integeration (6.04.04)

Type:	MECH

Description:	A cryogenic service platform must be provided in the assembly hall to support the detector cryogenics interface cryostat that services the maintenance area.

Provider:	Detector Infrastructure and Utilities Integration (6.03.01.09.04)

Details:	See details in the Detector Infrastructure Interface Control Document.

Requirements:	F-DET-INF.3

References:

I-DET-INF-INT.134	Hadron Polarimetry Facility

System 1:	Detector Infrastructure and Utilities Integration (6.03.01.09.04)

System 2:	IR System Installation and Final Integeration (6.04.04)

Type:	SPACE

Description:	Adequate space must be provided in the interaction region to support the hadron pC-polarimetry components and facility.

Provider:	Detector Infrastructure and Utilities Integration (6.03.01.09.04)

Details:	See details in the Detector Infrastructure Interface Control Document.

Requirements:	F-DET-INF.3

References:

# Applicable Documents

List applicable documents considered to be part of this document. Applicable documents shall be obtained from the EIC SharePoint Document Center.

# Detailed change Log

| Revision | Date | Change |
| --- | --- | --- |

# References

- doi:10.17226/25171., National Academies of Sciences, Engineering, and Medicine, "An Assessment of U.S.-Based Electron-Ion Collider Science", The National Academies Press, Washington, DC, 2018.

- EIC-ORG-PLN-010, Electron-Ion Collider L1 Requirements (Global Requirements Document)

- BNL-221006-2021-FORE, EIC Conceptual Design Report

- arXiv:2103.05419, Science Requirements and Detector Concepts for the Electron-Ion Collider: EIC Yellow Report

- EIC-SEG-PLN-016, Requirements Management Plan

- EIC-SEG-PLN-022, Systems Engineering Management Plan

- EIC-SEG-PLN-020, EIC Interface Management Plan